## System-Level-Equipment
Worksheet 1 - System Level Equipment Sizing Data
[6 empty] | Central Cooling Coil | [16 empty] | Central Heating Coil | [6 empty] | Precool Coil | [10 empty] | Preheat Coil | [6 empty] | Humidifier |  |  |  | Dehumidification Reheat Coil | [6 empty] | Supply Fan | [6 empty] | Return Fan | [5 empty] | Outdoor Ventilation Air
Alternative Name | System Name | Equipment Type | System Type | Total Floor Area (sqft) | Number of Zones | Total Coil Load (MBH) | Sensible Coil Load (MBH) | Latent Coil Load (MBH) | Coil Airflow at Peak Time (CFM) | Sum of Peak Zone Airflows (CFM) | Sensible Heat Ratio | Coil Water Flow Rate (gpm) | Time of Peak Coil Load | OA DB at Peak Time (F) | OA WB at Peak Time (F) | Coil Entering DB (F) | Coil Entering WB (F) | Coil Leaving DB (F) | Coil Leaving WB (F) | CFM/Ton | sqft/Ton | BTU/(hr sqft) | Peak Coil Load (MBH) | Coil Airflow at Peak Time (CFM) | Max Coil Airflow (CFM) | Coil Water Flow Rate (gpm) | Time of Peak Coil Load | Coil Entering DB (F) | Coil Leaving DB (F) | Total Coil Load (MBH) | Sensible Coil Load (MBH) | Latent Coil Load (MBH) | Coil Airflow at Peak Time (CFM) | Max Coil Airflow (CFM) | Coil Water Flow Rate (gpm) | Time of Peak Coil Load | Coil Entering DB (F) | Coil Entering WB (F) | Coil Leaving DB (F) | Coil Leaving WB (F) | Peak Coil Load (MBH) | Coil Airflow at Peak Time (CFM) | Max Coil Airflow (CFM) | Coil Water Flow Rate (gpm) | Time of Peak Coil Load | Coil Entering DB (F) | Coil Leaving DB (F) | Max Steam Flow Rate (lb/hr) | Air Volumetric Airflow (CFM) | Air Mass Flow Rate (lb/hr) | Moisture Gain (lb/lb) | Peak Coil Load (MBH) | Coil Airflow Rate (CFM) | Max Coil Airflow Rate (CFM) | Water Flow Rate (gpm) | Time of Peak Load | Coil Entering DB (F) | Coil Leaving DB (F) | Peak Airflow Rate (CFM) | Time of Peak Airflow | VAV Fan Diversity (%) | Fan BHP | Fan Motor kW | Fan Total Static (in wg) | CFM/sqft | Peak Airflow Rate (CFM) | Time of Peak Airflow | Fan BHP | Fan Motor kW | Fan Total Static (in wg) | CFM/sqft | Outoor Air Intake Flow Rate (CFM) | CFM/sqft | CFM/person | Percent Outdoor Air (%)
Default Alternative | AC-MECH/ELEC | SPLT AHU | SZCAV | 330 | 1 | 9.4 | 9.4 | 0 | 655 | 655 | 1 |  | SEP 1500 | 101 | 63.2 | 68 | 51.4 | 53.5 | 45.2 | 840.2 | 423.29 | 28.35 | [36 empty] | 655 |  |  | 0.359 | 0.285 | 2 | 1.99 | [6 empty] | 0 | 0 | 0 | 0
Default Alternative | AC-PBX/IT | SPLT AHU | SZCAV | 184.6 | 1 | 8.5 | 8.5 | 0 | 587 | 587 | 1 |  | JUL 2000 | 96.3 | 63.1 | 68 | 53.2 | 53.3 | 47.1 | 828.1 | 260.44 | 46.08 | [36 empty] | 587 |  |  | 0.322 | 0.255 | 2 | 3.18 | [6 empty] | 0 | 0 | 0 | 0
Default Alternative | HP-101-FITNESS | SPLT AHU | SZCAV | 1279.5 | 1 | 38.4 | 35 | 3.4 | 1464 | 1464 | 0.912 |  | JUL 1600 | 106.2 | 66.2 | 80.5 | 65.1 | 56.4 | 56.3 | 458 | 400.2 | 29.99 | 21.5 | 1464 | 1464 |  | DES HTG | 60.1 | 75.2 | [29 empty] | 1464 |  |  | 0.802 | 0.636 | 2 | 1.14 | [6 empty] | 335 | 0.26 | 26.2 | 22.9
Default Alternative | HP-102-OFFICES | SPLT AHU | SZCAV | 774 | 1 | 8.8 | 8.8 | 0 | 332 | 332 | 1 |  | JUL 1600 | 106.2 | 66.2 | 80.2 | 61.7 | 53.4 | 51.9 | 453.1 | 1055 | 11.37 | 6.4 | 332 | 332 |  | DES HTG | 60.7 | 80.4 | [29 empty] | 332 |  |  | 0.182 | 0.144 | 2 | 0.43 | [6 empty] | 73 | 0.09 | 13.83 | 21.9
Default Alternative | HP-103-BOH EMPLOYEE | SPLT AHU | SZCAV | 593.7 | 1 | 13.3 | 13.3 | 0 | 584 | 584 | 1 |  | SEP 1500 | 101 | 63.2 | 76.8 | 59.3 | 53.7 | 50.6 | 526.7 | 535.23 | 22.42 | 7.3 | 584 | 584 |  | DES HTG | 64.9 | 77.7 | [29 empty] | 584 |  |  | 0.32 | 0.254 | 2 | 0.98 | [6 empty] | 80 | 0.14 | 8.27 | 13.8
Default Alternative | HP-104-BOH LAUNDRY | SPLT AHU | SZCAV | 1317.5 | 1 | 31.4 | 30.6 | 0.9 | 1293 | 1293 | 0.972 |  | AUG 1500 | 106.2 | 66.2 | 77.8 | 62.5 | 53.9 | 53.8 | 493.5 | 503.01 | 23.86 | 14.3 | 1293 | 1293 |  | DES HTG | 64.5 | 75.8 | [29 empty] | 1293 |  |  | 0.708 | 0.562 | 2 | 0.98 | [6 empty] | 188 | 0.14 | 18.99 | 14.5
Default Alternative | HP-105-LOBBY/MARKET | SPLT AHU | SZCAV | 1301.9 | 1 | 29.6 | 29 | 0.6 | 917 | 917 | 0.98 |  | JUL 1600 | 106.2 | 66.2 | 83.6 | 63.3 | 51.7 | 51.6 | 371.9 | 527.8 | 22.74 | 23.4 | 917 | 917 |  | DES HTG | 55.2 | 81.3 | [29 empty] | 917 |  |  | 0.503 | 0.399 | 2 | 0.7 | [6 empty] | 298 | 0.23 | 10.17 | 32.5
Default Alternative | HP-106-DINING LARGE | SPLT AHU | SZCAV | 1092.2 | 1 | 34.6 | 34.6 | 0 | 832 | 832 | 1 |  | JUL 1600 | 106.2 | 66.2 | 93.7 | 63.6 | 51.6 | 48 | 289 | 379.22 | 31.64 | 34.5 | 832 | 832 |  | DES HTG | 39.4 | 81.9 | [29 empty] | 832 |  |  | 0.456 | 0.362 | 2 | 0.76 | [6 empty] | 524 | 0.48 | 12 | 63
Default Alternative | HP-107-BUFFET/SERVING | SPLT AHU | SZCAV | 747 | 1 | 23.3 | 23.3 | 0 | 779 | 779 | 1 |  | JUL 1600 | 106.2 | 66.2 | 82.4 | 61.5 | 52.1 | 50.3 | 401 | 384.31 | 31.23 | 14.9 | 779 | 779 |  | DES HTG | 57.1 | 76.7 | [29 empty] | 779 |  |  | 0.427 | 0.339 | 2 | 1.04 | [6 empty] | 224 | 0.3 | 22.5 | 28.8
Default Alternative | HP-108-FOOD PREP | SPLT AHU | SZCAV | 695.6 | 1 | 36.6 | 36.6 | 0 | 1080 | 1080 | 1 |  | JUL 1600 | 106.2 | 66.2 | 87.8 | 61.9 | 53.5 | 49.1 | 354.5 | 228.31 | 52.56 | 26.6 | 1080 | 1080 |  | DES HTG | 48.6 | 73.9 | [29 empty] | 1080 |  |  | 0.592 | 0.469 | 2 | 1.55 | [6 empty] | 487 | 0.7 | 35 | 45.1
Default Alternative | HP-109-DINING FLEX | SPLT AHU | SZCAV | 362.7 | 1 | 12.9 | 12.9 | 0 | 361 | 361 | 1 |  | AUG 1500 | 106.2 | 66.2 | 88.9 | 62.5 | 52.8 | 49.2 | 337.4 | 338.67 | 35.43 | 11.4 | 361 | 361 |  | DES HTG | 47 | 79.4 | [29 empty] | 361 |  |  | 0.198 | 0.157 | 2 | 1 | [6 empty] | 174 | 0.48 | 12 | 48.2
Default Alternative | HP-110-DINING SMALL | SPLT AHU | SZCAV | 713 | 1 | 24.5 | 24.5 | 0 | 703 | 703 | 1 |  | AUG 1400 | 104.9 | 65.8 | 88.5 | 62.4 | 53.2 | 49.3 | 344.1 | 349.12 | 34.37 | 22.4 | 703 | 703 |  | DES HTG | 46.8 | 79.5 | [29 empty] | 703 |  |  | 0.385 | 0.305 | 2 | 0.99 | [6 empty] | 342 | 0.48 | 12 | 48.7
Default Alternative | HP-111-MEETING | SPLT AHU | SZCAV | 808.8 | 1 | 29.4 | 28.4 | 1 | 1281 | 1281 | 0.968 |  | SEP 1400 | 99.7 | 62.8 | 76.7 | 62.3 | 54.3 | 54.1 | 523.6 | 330.62 | 36.29 | 15.3 | 1281 | 1281 |  | DES HTG | 64.7 | 77 | [29 empty] | 1281 |  |  | 0.701 | 0.556 | 2 | 1.58 | [6 empty] | 180 | 0.22 | 6.84 | 14.1
Default Alternative | HP-112-ENGINEERING | SPLT AHU | SZCAV | 232.6 | 1 | 2.4 | 2.4 | 0 | 77 | 77 | 1 |  | JUL 1600 | 106.2 | 66.2 | 82.9 | 62.5 | 51.4 | 51.1 | 385.9 | 1160.27 | 10.34 | 1.5 | 77 | 77 |  | DES HTG | 56.4 | 76.6 | [29 empty] | 77 |  |  | 0.042 | 0.034 | 2 | 0.33 | [6 empty] | 23 | 0.1 | 12.5 | 30.1
Default Alternative | HP-STAIRS1 | SPLT AHU | SZCAV | 992.6 | 1 | 11.7 | 11.7 | 0 | 512 | 512 | 1 |  | JUL 1300 | 102.9 | 65.2 | 73 | 55.2 | 49.7 | 45.5 | 523.9 | 1016.44 | 11.81 | 8.4 | 512 | 512 |  | DES HTG | 72 | 88.9 | [29 empty] | 512 |  |  | 0.28 | 0.222 | 2 | 0.52 | [6 empty] | 0 | 0 | 0 | 0
Default Alternative | HP-STAIRS2 | SPLT AHU | SZCAV | 1000.7 | 1 | 14.3 | 14.3 | 0 | 607 | 607 | 1 |  | JUL 1900 | 100.1 | 64.3 | 73 | 55.2 | 49.1 | 45.2 | 509.8 | 840.65 | 14.27 | 8.6 | 607 | 607 |  | DES HTG | 72 | 86.5 | [29 empty] | 607 |  |  | 0.332 | 0.264 | 2 | 0.61 | [6 empty] | 0 | 0 | 0 | 0
Default Alternative | UH-FIRE RISER | UNDEFINED | SZCAV | 35 | 1 | [17 empty] | 0.8 | 48 | 48 | 0.08 | DES HTG | 69.7 | 86.6 | [29 empty] | 48 |  |  | 0.026 | 0.021 | 2 | 1.38 | [6 empty] | 2 | 0.06 | 0 | 4.3
Default Alternative | UH-POOL EQUIP STORAGE | UNDEFINED | SZCAV | 102.9 | 1 | [17 empty] | 1.5 | 75 | 75 | 0.15 | DES HTG | 67.7 | 88.4 | [29 empty] | 75 |  |  | 0.041 | 0.033 | 2 | 0.73 | [6 empty] | 6 | 0.06 | 0 | 8.2
Default Alternative | UH-VESTIBULE | UNDEFINED | SZCAV | 155.1 | 1 | [17 empty] | 3.3 | 170 | 170 | 0.33 | DES HTG | 69.2 | 89.3 | [29 empty] | 170 |  |  | 0.093 | 0.074 | 2 | 1.1 | [6 empty] | 9 | 0.06 | 0 | 5.5

## DOAS-AHU
Worksheet 2 - DOAS Air Handler Sizing Data
[6 empty] | Cooling Coil | [15 empty] | Heating Coil | [6 empty] | Humidifier |  |  |  | Dehumidification Reheat Coil | [6 empty] | Ventilation Fan |  |  |  |  | Exhaust Fan |  |  |  |  | Outdoor Ventilation Air
Alternative Name | System Name | Equipment Type | System Type | Total Floor Area (sqft) | Number of Zones | Total Coil Load (MBH) | Sensible Coil Load (MBH) | Latent Coil Load (MBH) | Coil Airflow at Peak Time (CFM) | Max Coil Airflow (CFM) | Coil Water Flow Rate (gpm) | Time of Peak Coil Load | OA DB at Peak Time (F) | OA WB at Peak Time (F) | Coil Entering DB (F) | Coil Entering WB (F) | Coil Leaving DB (F) | Coil Leaving WB (F) | CFM/Ton | sqft/Ton | BTU/(hr sqft) | Peak Coil Load (MBH) | Coil Airflow at Peak Time (CFM) | Max Coil Airflow (CFM) | Coil Water Flow Rate (gpm) | Time of Peak Coil Load | Coil Entering DB (F) | Coil Leaving DB (F) | Max Steam Flow Rate (lb/hr) | Air Volumetric Airflow (CFM) | Air Mass Flow Rate (lb/hr) | Moisture Gain (lb/lb) | Peak Coil Load (MBH) | Coil Airflow Rate (CFM) | Max Coil Airflow Rate (CFM) | Water Flow Rate (gpm) | Time of Peak Load | Coil Entering DB (F) | Coil Leaving DB (F) | Peak Airflow Rate (CFM) | Fan BHP | Fan Motor kW | Fan Total Static (in wg) | CFM/sqft | Peak Airflow Rate (CFM) | Fan BHP | Fan Motor kW | Fan Total Static (in wg) | CFM/sqft | Outoor Air Intake Flow Rate (CFM) | CFM/sqft | CFM/person | Percent Outdoor Air (%)
Default Alternative | DOAS-1-CORRIDORS ONLY | PKG RTU | MUA/DOAS | 12123.5 | 1 | 18.5 | 18.5 | 0 | 708 | 708 |  | JUL 1500 | 106.2 | 66.2 | 100 | 64.4 | 73.5 | 55.4 | 460 | 7881.77 | 1.52 | 24.4 | 708 | 708 |  | DES HTG | 32.9 | 68.5 | [11 empty] | 708 | 0.388 | 0.307 | 2 | 0.06 | 708 | 0 | 0 | 0 | 0.06 | 708 | 0.06 | 143.99 | 100
Default Alternative | UNIT KING | TERM UNITS | PKG-FCU | 353.3 | 1 | 1.2 | 1.2 | 0 | 39 | 39 |  | JUL 1500 | 106.2 | 66.2 | 106.1 | 66.2 | 73.5 | 55.4 | 374.2 | 3401.59 | 3.53 | 1.8 | 39 | 39 |  | DES HTG | 20 | 68.5 | [11 empty] | 39 | 0.021 | 0.017 | 2 | 0.11 | [5 empty] | 39 | 0.11 | 11 | 100
Default Alternative | UNIT QQ | TERM UNITS | PKG-FCU | 454.7 | 1 | 1.6 | 1.6 | 0 | 50 | 50 |  | JUL 1500 | 106.2 | 66.2 | 106.1 | 66.2 | 73.5 | 55.4 | 374.2 | 3401.59 | 3.53 | 2.4 | 50 | 50 |  | DES HTG | 20 | 68.5 | [11 empty] | 50 | 0.027 | 0.022 | 2 | 0.11 | [5 empty] | 50 | 0.11 | 11 | 100
Default Alternative | UNIT QQ XXL | TERM UNITS | PKG-FCU | 444.8 | 1 | 1.6 | 1.6 | 0 | 49 | 49 |  | JUL 1500 | 106.2 | 66.2 | 106.1 | 66.2 | 73.5 | 55.4 | 374.2 | 3401.59 | 3.53 | 2.3 | 49 | 49 |  | DES HTG | 20 | 68.5 | [11 empty] | 49 | 0.027 | 0.021 | 2 | 0.11 | [5 empty] | 49 | 0.11 | 11 | 100