## Zone-Air-Terminal-Sizing
Worksheet 1 - Zone Air Terminal Sizing Data
Alternative Name | System Name | Zone Name | Terminal Type | Design Supply Airflow (CFM) | Minimum Supply Airflow (CFM) | Reheat Coil Capacity (MBH) | Reheat Coil Water Flow (gpm) | Zone Heating Unit Capacity (MBH) | Zone Heating Unit Water Flow (gpm) | Mixing Box Fan Airflow (CFM) | Zone Floor Area (sqft) | CFM/sqft
Default Alternative | HP-101-FITNESS | HP-101-FITNESS | Diffuser | 1464 | 1464 | 0 |  | 0 |  | 0 | 1279.5 | 1.14
Default Alternative | HP-102-OFFICES | HP-102-OFFICES | Diffuser | 332 | 332 | 0 |  | 0 |  | 0 | 774 | 0.43
Default Alternative | HP-103-BOH EMPLOYEE | HP-103-BOH EMPLOYEE | Diffuser | 584 | 584 | 0 |  | 0 |  | 0 | 593.7 | 0.98
Default Alternative | HP-104-BOH LAUNDRY | HP-104-BOH LAUNDRY | Diffuser | 1293 | 1293 | 0 |  | 0 |  | 0 | 1317.5 | 0.98
Default Alternative | HP-105-LOBBY/MARKET | HP-105-LOBBY/MARKET | Diffuser | 917 | 917 | 0 |  | 0 |  | 0 | 1301.9 | 0.7
Default Alternative | HP-106-DINING LARGE | HP-106-DINING LARGE | Diffuser | 832 | 832 | 0 |  | 0 |  | 0 | 1092.2 | 0.76
Default Alternative | HP-107-BUFFET/SERVING | HP-107-BUFFET/SERVING | Diffuser | 779 | 779 | 0 |  | 0 |  | 0 | 747 | 1.04
Default Alternative | HP-108-FOOD PREP | HP-108-FOOD PREP | Diffuser | 1080 | 1080 | 0 |  | 0 |  | 0 | 695.6 | 1.55
Default Alternative | HP-109-DINING FLEX | HP-109-DINING FLEX | Diffuser | 361 | 361 | 0 |  | 0 |  | 0 | 362.7 | 1
Default Alternative | HP-110-DINING SMALL | HP-110-DINING SMALL | Diffuser | 703 | 703 | 0 |  | 0 |  | 0 | 713 | 0.99
Default Alternative | HP-111-MEETING | HP-111-MEETING | Diffuser | 1281 | 1281 | 0 |  | 0 |  | 0 | 808.8 | 1.58
Default Alternative | HP-112-ENGINEERING | HP-112-ENGINEERING | Diffuser | 77 | 77 | 0 |  | 0 |  | 0 | 232.6 | 0.33
Default Alternative | HP-STAIRS1 | HP-STAIRS1 | Diffuser | 512 | 512 | 0 |  | 0 |  | 0 | 992.6 | 0.52
Default Alternative | HP-STAIRS2 | HP-STAIRS2 | Diffuser | 607 | 607 | 0 |  | 0 |  | 0 | 1000.7 | 0.61
Default Alternative | UH-FIRE RISER | UH-FIRE RISER | Diffuser | 48 | 48 | 0 |  | 0 |  | 0 | 35 | 1.38
Default Alternative | UH-POOL EQUIP STORAGE | UH-POOL STORAGE | Diffuser | 75 | 75 | 0 |  | 0 |  | 0 | 102.9 | 0.73
Default Alternative | UH-VESTIBULE | UH-01-VESTIBULE | Diffuser | 170 | 170 | 0 |  | 0 |  | 0 | 155.1 | 1.1

## Zone-Terminal-Unit-Sizing
Worksheet 2 - Zone Terminal Unit Sizing Data
[5 empty] | Cooling Coil | [11 empty] | Heating Coil |  |  |  | Supply Air |  |  |  | OA Vent Design Airflow |  | Primary Supply Airflow
Alternative Name | System Name | Zone Name | Zone Floor Area (sqft) | Terminal Type | Total Coil Load (MBH) | Sensible Coil Load (MBH) | Latent Coil Load (MBH) | Time of Peak Coil Load | Coil Water Flow Rate (gpm) | Coil Entering DB (F) | Coil Entering WB (F) | Coil Leaving DB (F) | Coil Leaving WB (F) | CFM/sqft | sqft/Ton | BTU/(hr sqft) | Peak Coil Load (MBH) | Coil Water Flow Rate (gpm) | Coil Entering DB (F) | Coil Leaving DB (F) | Design Supply Airflow (CFM) | Fan BHP | Fan Motor kW | CFM/sqft | CFM | CFM/sqft | CFM | CFM/sqft
Default Alternative | UNIT KING | UNIT KING | 353.3 | Fan Coil | 6.7 | 6.4 | 0.3 | JUL 1900 |  | 73.4 | 56.6 | 56.7 | 49.7 | 1.1 | 629.25 | 19.07 | 3.3 |  | 72 | 80.6 | 390 | 0.029 | 0.023 | 1.1 | 39 | 0.11
Default Alternative | UNIT QQ | UNIT QQ | 454.7 | Fan Coil | 8.3 | 8 | 0.3 | AUG 1400 |  | 73.4 | 56.6 | 57.4 | 50.2 | 1.11 | 658.11 | 18.23 | 3.8 |  | 72 | 79.8 | 506 | 0.037 | 0.03 | 1.11 | 50 | 0.11
Default Alternative | UNIT QQ XXL | UNIT QQ XXL | 444.8 | Fan Coil | 8.1 | 7.9 | 0.2 | SEP 1400 |  | 73.4 | 55.9 | 57.1 | 49.3 | 1.11 | 662.14 | 18.12 | 3.7 |  | 72 | 79.7 | 493 | 0.036 | 0.029 | 1.11 | 49 | 0.11

## Zone-Loads
Worksheet 3 - Peak Zone Loads
Alternative Name | System Name | Zone Name | Peak Sensible Clg Load (BTU/hr) | Latent Clg Load (BTU/hr) | Time of Peak Sensible Clg Load | Sensible Htg Load (BTU/hr) | Occ. Clg Setpoint (F) | Occ. Htg Setpoint (F) | Zone Floor Area (sqft) | CFM/sqft
Default Alternative | HP-101-FITNESS | HP-101-FITNESS | 21291 | 12918 | JUN 1900 | 5449 | 73 | 72 | 1279.5 | 1.14
Default Alternative | HP-102-OFFICES | HP-102-OFFICES | 5301 | 1079 | JUN 2000 | 2573 | 73 | 72 | 774 | 0.43
Default Alternative | HP-103-BOH EMPLOYEE | HP-103-BOH EMPLOYEE | 10168 | 1167 | OCT 1400 | 3882 | 73 | 72 | 593.7 | 0.98
Default Alternative | HP-104-BOH LAUNDRY | HP-104-BOH LAUNDRY | 21939 | 4502 | AUG 1400 | 6042 | 73 | 72 | 1317.5 | 0.98
Default Alternative | HP-105-LOBBY/MARKET | HP-105-LOBBY/MARKET | 15953 | 6008 | JUL 1800 | 8007 | 73 | 72 | 1301.9 | 0.7
Default Alternative | HP-106-DINING LARGE | HP-106-DINING LARGE | 14537 | 5243 | JUL 1600 | 7919 | 73 | 72 | 1092.2 | 0.76
Default Alternative | HP-107-BUFFET/SERVING | HP-107-BUFFET/SERVING | 13612 | 2689 | JUL 1800 | 3495 | 73 | 72 | 747 | 1.04
Default Alternative | HP-108-FOOD PREP | HP-108-FOOD PREP | 18860 | 3756 | JUL 2000 | 3110 | 73 | 72 | 695.6 | 1.55
Default Alternative | HP-109-DINING FLEX | HP-109-DINING FLEX | 6310 | 1741 | SEP 1300 | 2532 | 73 | 72 | 362.7 | 1
Default Alternative | HP-110-DINING SMALL | HP-110-DINING SMALL | 12271 | 3422 | OCT 1300 | 5058 | 73 | 72 | 713 | 0.99
Default Alternative | HP-111-MEETING | HP-111-MEETING | 22128 | 5403 | NOV 1300 | 7075 | 73 | 72 | 808.8 | 1.58
Default Alternative | HP-112-ENGINEERING | HP-112-ENGINEERING | 1351 | 381 | JUL 1900 | 437 | 73 | 72 | 232.6 | 0.33
Default Alternative | HP-STAIRS1 | HP-STAIRS1 | 8312 | 0 | JUL 1200 | 7281 | 73 | 72 | 992.6 | 0.52
Default Alternative | HP-STAIRS2 | HP-STAIRS2 | 10568 | 0 | AUG 1800 | 7379 | 73 | 72 | 1000.7 | 0.61
Default Alternative | UH-FIRE RISER | UH-FIRE RISER | 0 | 0 | MAR 1200 | 844 | 75 | 72 | 35 | 1.38
Default Alternative | UH-POOL EQUIP STORAGE | UH-POOL STORAGE | 0 | 0 | NOV 2300 | 1309 | 75 | 72 | 102.9 | 0.73
Default Alternative | UH-VESTIBULE | UH-01-VESTIBULE | 0 | 0 | MAY 0600 | 2967 | 75 | 72 | 155.1 | 1.1
Default Alternative | UNIT KING | UNIT KING | 5677 | 424 | JUN 1900 | 2638 | 73 | 72 | 353.3 | 1.1
Default Alternative | UNIT QQ | UNIT QQ | 7365 | 546 | SEP 1400 | 3056 | 73 | 72 | 454.7 | 1.11
Default Alternative | UNIT QQ XXL | UNIT QQ XXL | 7174 | 534 | SEP 1400 | 2876 | 73 | 72 | 444.8 | 1.11

## Space-Loads
Worksheet 4 - Peak Space Loads
Alternative Name | System Name | Zone Name | Space Name | Peak Sensible Clg Load (BTU/hr) | Latent Clg Load (BTU/hr) | Time of Peak Sensible Clg Load | Peak Sensible Htg Load (BTU/hr) | Supply Airflow Rate (CFM) | Occ. Clg Setpoint (F) | Occ. Htg Setpoint (F) | Space Floor Area (sqft) | CFM/sqft
Default Alternative | HP-101-FITNESS | HP-101-FITNESS | 141-FITNESS | 17403 | 12181 | JUN 1900 | 5029 | 1196 | 73 | 72 | 1117.5 | 1.07
Default Alternative | HP-101-FITNESS | HP-101-FITNESS | 142-GUEST LAUNDRY | 3906 | 737 | JUL 1800 | 419 | 268 | 73 | 72 | 162 | 1.66
Default Alternative | HP-102-OFFICES | HP-102-OFFICES | 119-SALES OFFICE | 762 | 205 | JUL 1900 | 119 | 44 | 73 | 72 | 109.9 | 0.4
Default Alternative | HP-102-OFFICES | HP-102-OFFICES | 119-WORK AREA | 2480 | 669 | JUL 1900 | 303 | 142 | 73 | 72 | 407.7 | 0.35
Default Alternative | HP-102-OFFICES | HP-102-OFFICES | 122-GM OFFICE | 1016 | 205 | JUL 1800 | 652 | 58 | 73 | 72 | 120.3 | 0.48
Default Alternative | HP-102-OFFICES | HP-102-OFFICES | 123-CLOSET | 87 | 0 | JUL 2000 | 38 | 5 | 73 | 72 | 25.2 | 0.2
Default Alternative | HP-102-OFFICES | HP-102-OFFICES | 124-RETAIL STORAGE | 1006 | 0 | JUN 2100 | 1461 | 84 | 73 | 72 | 110.9 | 0.75
Default Alternative | HP-103-BOH EMPLOYEE | HP-103-BOH EMPLOYEE | 125-BOH CORRIDOR | 321 | 0 | JUL 1900 | 122 | 18 | 73 | 72 | 140.3 | 0.13
Default Alternative | HP-103-BOH EMPLOYEE | HP-103-BOH EMPLOYEE | 132-BREAK ROOM | 9716 | 1167 | OCT 1400 | 3711 | 556 | 73 | 72 | 389.1 | 1.43
Default Alternative | HP-103-BOH EMPLOYEE | HP-103-BOH EMPLOYEE | 133-STAFF RR | 166 | 0 | SEP 1700 | 49 | 10 | 73 | 72 | 64.3 | 0.15
Default Alternative | HP-104-BOH LAUNDRY | HP-104-BOH LAUNDRY | 126-BOH LAUNDRY | 14506 | 3966 | AUG 1300 | 2683 | 831 | 73 | 72 | 871.6 | 0.95
Default Alternative | HP-104-BOH LAUNDRY | HP-104-BOH LAUNDRY | 127 - DRYER ENCLOSURE | 5553 | 536 | SEP 1600 | 1136 | 318 | 73 | 72 | 117.8 | 2.7
Default Alternative | HP-104-BOH LAUNDRY | HP-104-BOH LAUNDRY | 128-LINEN STORAGE | 1777 | 0 | AUG 1300 | 2074 | 119 | 73 | 72 | 171.4 | 0.69
Default Alternative | HP-104-BOH LAUNDRY | HP-104-BOH LAUNDRY | 129-STORAGE | 152 | 0 | JUL 2000 | 51 | 9 | 73 | 72 | 48.6 | 0.18
Default Alternative | HP-104-BOH LAUNDRY | HP-104-BOH LAUNDRY | 130-LINEN CLOSET | 288 | 0 | JUL 2000 | 99 | 17 | 73 | 72 | 108.1 | 0.15
Default Alternative | HP-105-LOBBY/MARKET | HP-105-LOBBY/MARKET | 101/102-MARKET/RECEPTION | 10111 | 4008 | JUN 1800 | 5243 | 579 | 73 | 72 | 651 | 0.89
Default Alternative | HP-105-LOBBY/MARKET | HP-105-LOBBY/MARKET | 103-LOBBY (entry) | 5912 | 2001 | JUL 1700 | 2765 | 338 | 73 | 72 | 650.9 | 0.52
Default Alternative | HP-106-DINING LARGE | HP-106-DINING LARGE | 105A DINING | 14537 | 5243 | JUL 1600 | 7919 | 832 | 73 | 72 | 1092.2 | 0.76
Default Alternative | HP-107-BUFFET/SERVING | HP-107-BUFFET/SERVING | 106-BREAKFAST/BUFFETT | 13612 | 2689 | JUL 1800 | 3495 | 779 | 73 | 72 | 747 | 1.04
Default Alternative | HP-108-FOOD PREP | HP-108-FOOD PREP | 107-FOOD PREP | 18860 | 3756 | JUL 2000 | 3110 | 1080 | 73 | 72 | 695.6 | 1.55
Default Alternative | HP-109-DINING FLEX | HP-109-DINING FLEX | 109-DINING/FLEX | 6310 | 1741 | SEP 1300 | 2532 | 361 | 73 | 72 | 362.7 | 1
Default Alternative | HP-110-DINING SMALL | HP-110-DINING SMALL | 105B - DINING | 12271 | 3422 | OCT 1300 | 5058 | 703 | 73 | 72 | 713 | 0.99
Default Alternative | HP-111-MEETING | HP-111-MEETING | 111-MEETING ROOM | 19953 | 5403 | NOV 1300 | 5451 | 1142 | 73 | 72 | 658.9 | 1.73
Default Alternative | HP-111-MEETING | HP-111-MEETING | 111-MEETING STORAGE | 2414 | 0 | SEP 1600 | 1624 | 138 | 73 | 72 | 149.9 | 0.92
Default Alternative | HP-112-ENGINEERING | HP-112-ENGINEERING | 134-ENGINEERING | 1351 | 381 | JUL 1900 | 437 | 77 | 73 | 72 | 232.6 | 0.33
Default Alternative | HP-STAIRS1 | HP-STAIRS1 | 109-STAIRS 1 | 1851 | 0 | JUL 1200 | 2429 | 139 | 73 | 72 | 196 | 0.71
Default Alternative | HP-STAIRS1 | HP-STAIRS1 | 200-STAIRS 1 | 1578 | 0 | JUL 1200 | 1136 | 90 | 73 | 72 | 196 | 0.46
Default Alternative | HP-STAIRS1 | HP-STAIRS1 | 300-STAIRS 1 | 1567 | 0 | JUL 1200 | 1113 | 90 | 73 | 72 | 201.7 | 0.44
Default Alternative | HP-STAIRS1 | HP-STAIRS1 | 400-STAIRS 1 | 1573 | 0 | JUL 1200 | 1121 | 90 | 73 | 72 | 203.1 | 0.44
Default Alternative | HP-STAIRS1 | HP-STAIRS1 | 500-STAIRS 1 | 1789 | 0 | JUL 1300 | 1483 | 102 | 73 | 72 | 196 | 0.52
Default Alternative | HP-STAIRS2 | HP-STAIRS2 | 143-STAIRS 2 | 2459 | 0 | AUG 1800 | 2464 | 141 | 73 | 72 | 201.3 | 0.7
Default Alternative | HP-STAIRS2 | HP-STAIRS2 | 210-STAIRS 2 | 1960 | 0 | AUG 1900 | 1149 | 112 | 73 | 72 | 202.7 | 0.55
Default Alternative | HP-STAIRS2 | HP-STAIRS2 | 310-STAIRS 2 | 1953 | 0 | AUG 1900 | 1141 | 112 | 73 | 72 | 198.6 | 0.56
Default Alternative | HP-STAIRS2 | HP-STAIRS2 | 410-STAIRS 2 | 1916 | 0 | AUG 1900 | 1125 | 110 | 73 | 72 | 199.1 | 0.55
Default Alternative | HP-STAIRS2 | HP-STAIRS2 | 510 STAIRS 2 | 2307 | 0 | AUG 1800 | 1502 | 132 | 73 | 72 | 199.1 | 0.66
Default Alternative | UH-FIRE RISER | UH-FIRE RISER | 136-FIRE RISER | 0 | 0 | MAR 1200 | 844 | 48 | 75 | 72 | 35 | 1.38
Default Alternative | UH-POOL EQUIP STORAGE | UH-POOL STORAGE | POOL STORAGE | 0 | 0 | NOV 2300 | 1309 | 75 | 75 | 72 | 102.9 | 0.73
Default Alternative | UH-VESTIBULE | UH-01-VESTIBULE | 100-VESTIBULE | 0 | 0 | MAY 0600 | 2967 | 170 | 75 | 72 | 155.1 | 1.1
Default Alternative | UNIT KING | UNIT KING | UNIT 533-KING | 5677 | 424 | JUN 1900 | 2638 | 390 | 73 | 72 | 353.3 | 1.1
Default Alternative | UNIT QQ | UNIT QQ | UNIT 516-QQ | 7365 | 546 | SEP 1400 | 3056 | 506 | 73 | 72 | 454.7 | 1.11
Default Alternative | UNIT QQ XXL | UNIT QQ XXL | UNIT 500 - QQ XXL | 7174 | 534 | SEP 1400 | 2876 | 493 | 73 | 72 | 444.8 | 1.11